## MBIO2IEC104
Name | Object Type | Access | Timestamp | Start IOA | Data Quantity | Interrogation Group | Counter Group | IEC104 Data Exchange | Deadband Value | Report Start Type | Interval For Report | Alarm | Alarm Upper Bound | Upper Bound IOA | Alarm Lower Bound | Lower Bound IOA | Local I/O | Modbus Host | Modbus Port | Device ID | Function Code | Modbus Address | Polling Interval | Timeout | Address Bit | Data Type | Data Swap | Byte Swap | Data Multiplier | Data Offset
FC3_A | Bitstring of 32 bit | Read/Write | No time | 1 | 1 | 0 |  | Send on Request |  |  |  | No | [5 empty] | 192.168.1.102 | 502 | 1 | 3 | 1 | 10000 | 1000 |  | uint32 | None | No | 1 | 0
FC3_B | Bitstring of 32 bit | Read/Write | No time | 2 | 1 | 1 |  | Send on Request |  |  |  | No | [5 empty] | 192.168.1.103 | 502 | 2 | 3 | 1 | 10000 | 1000 |  | uint32 | None | No | 1 | 0
FC3_C | Bitstring of 32 bit | Read/Write | No time | 3 | 1 | 2 |  | Send on Request |  |  |  | No | [5 empty] | 192.168.1.104 | 502 | 3 | 3 | 1 | 10000 | 1000 |  | uint32 | None | No | 1 | 0
FC3_D | Bitstring of 32 bit | Read/Write | No time | 4 | 1 | 3 |  | Send on Request |  |  |  | No | [5 empty] | 192.168.1.105 | 502 | 4 | 3 | 1 | 10000 | 1000 |  | uint32 | None | No | 1 | 0
Note on A3: User defined description for the data point.
Note on B3: The data type defined in IEC60870-5 for each data point. Options: Single Point, Double Point, Bitstring of 32 bit, Measured Normalized Value, Measured Scaled Value, Measured Short Floating Point Value, Integrated Totals
Note on C3: The access right for the data point. Options: Read-Only, Write-Only, Read/Write.
Note on D3: Time Stamp Format for each data point. Options: No time, CP24Time2a, CP56Time2a
Note on E3: A unique Information Object Address for the data point.
Note on F3: The request address. Range: 1~2000
Note on G3: 0 for General Group; 1 for interrogation group 1; 2 for interrogation group 2; … etc.
Note on H3: 5 for general counter group; 1 for counter group 1; 2 for counter group 2; … etc
Note on I3: Decides when should send data to IEC104 client. Option: Send on Required only: Data will only be returned when asked. Cyclic Send: Periodically send data at the interval defined in "Polling Interval" field. Send on Change: Send data only when the data is chaned. Silence within Deadband: Send data only when the data changes exceed the deadband range.
Note on J3: When the difference between the data and the previous deadband instance is less than the databand value, the data is not sent to IEC104 client. Otherwise, the data will be sent, and will be the new deadband instance.
Note on K3: The Freeze Start Type parameter will define when the gateway starts sending the M_IT messages.
Note on L3: The time interval for spontaneous data reporting, measured in seconds. For instance, if "Report Start Type" is "Hour" and "Interval For Report" is set to 900, it means that within one hour, data will be reported every 15 minutes.
Note on M3: When the data is in alarm mode and exceeds the upper and lower bound, an alarm will be issued.
Note on N3: The upper bound of alarm threshold.
Note on P3: The lower bound of alarm threshold.
Note on R3: The Port that MODBUS RTU connection will be established on. If southbound protocol is Modbus/TCP, the filed MUST be empty.
Note on S3: Defines server address of the TCP server where data will be sent. If southbound protocol is Modbus RTU, the field MUST be empty.
Note on T3: TCP port of the server to send received data on. The 502 port is set by default. If southbound protocol is Modbus RTU, the field MUST be empty.
Note on U3: The Device ID indicates the recipient of the Modbus message. Range: 1~255
Note on V3: The Modbus function that are used to read or write data with Modbus server. Options: 1, 2, 3, 4, 5, 6, 15 and 16.
Note on W3: The Modbus Address that defines the location of data in a Modbus server. Range: 1~65535
Note on X3: The interval defines how often send Modbus query to read data from Modbus server and how often send the data to IEC104 client when "Cyclic Send", "Send on Change" or "Silence within Deadband" is selected in "IEC104 Data Exchange" field. Range: 10 ~ 10000000 ms
Note on Y3: The time span within which the Modbus server must return the Modbus response. Range: 100~ 10000 ms.
Note on AA3: Decides in what encoding type of the received/transmitted data. Option: boolean, int16, uint16, float16, int32, uint32, float32, int64, unit64, float64
Note on AB3: The Data Swap field determines the order in which the particular bytes of the received / transmitted data are delivered. Option:  None: 0x1a2b ⮕ 0x1a2b Word: 0x1a2b ⮕ 0x2b1a Double Word: 0x1a2b3c4d ⮕ 0x3c4d1a2b Double Word-Frame: 0x1a2b3c4d ⮕ 0x4d3c2b1a Quad Word: 0x1a2b3c4d5e6f7890 ⮕ 0x78905e6f3c4d1a2b
Note on AC3: Option: Yes, No When select Yes with Data Swap  None: 0x1a2b ⮕ 0xa1b2 Word: 0x1a2b ⮕ 0xb2a1 Double Word: 0x1a2b3c4d ⮕ 0xc3d4a1b2 Double Word-Frame: 0x1a2b3c4d ⮕ 0xd4c3b2a1 Quad Word: 0x1a2b3c4d5e6f7890 ⮕ 0x8709e5f6c3d4a1b2
Note on AD3: The value used to multiply the data value.
Note on AE3: The value used to add/substractthe data value.
CSV Check
CSV Export
CSV Import